## Slide 1
1. 双向重过载：量化评估与分阶段协同治理
以载流设备累积寿命损失量化风险，按问题持续性选择治理路径：
短时采用 EV–退役储能协同，长期采用光伏汇集与网络扩容。
按短时或长期问题分别治理，并回到同一评估体系；寿命损失、调控目标和规划成本各有明确含义
共同基础：双向潮流与风险量化
短时治理：有序充电与退役储能协同
长期治理：反向汇集与正向扩容协同
光伏出力
供电功率
时序运行状态
累积损伤
风险诊断
短时治理
长期治理
电价 / 等待
混合充电负荷
容量 / 出力
候选汇集点
修正净负荷
更新容量边界
联合方案
短时治理后再评估
长期治理后再评估
分布式光伏
EV与负荷
配变 / 线路
电流、环境温度
热模型与老化速率
日寿命损失 / 六项指标
治理
类型
用户选择
Logit
响应度 εev
AIW-PSO
配置与充放电
退役储能
DPV 集群
K-means
汇集站
选址定容
配变 / 线路
扩容
汇集＋扩容
寿命参考值24 h；重载 / 轻载均纳入
E：年投资成本−年收益；计及容量衰减
ΔFeq：偏离24 h；SOC、电压及载流约束
电费激励与等待时间共同影响响应
功率平衡 / 电压 / 标准容量约束
CPLEX交替求解：成本变化≤1% 或50次
年规划成本＝年汇集成本＋年扩容成本
AHP权重汇总为综合得分
Notes: Source: E:\application\xwechat_files\wxid_xyihcy7u0jkj21_d246\msg\file\2026-10\20261010170602.pdf
Method: PDF pp.22–23 (printed pp.9–10), Fig.2-1 p.24; Eqs.2-2–2-20 pp.28–32; Logit Eqs.3-13,3-14 p.41; Eqs.3-23,3-34 pp.43,46; AIW-PSO pp.48–50; collection/expansion pp.60–70. Each edge provenance in semantic-graph.json. The drawing is a conceptual assessment–treatment–reassessment framework, not a single numerical algorithm. Short and long pathways are alternatives. The source describes a grey prediction route, but the reported long-term case directly scales resources and load (PDF p.71). No independent experiment reproduction is claimed.

## Slide 2
2. IEEE 33节点算例：评估、短时调控与长期规划
三项工作分别验证：季节风险可区分，有序充电降低储能配置需求，汇集–扩容缓解长期重过载。
各章采用对应场景与评价口径，综合得分表示整体影响，不是风险概率。
仿真基于改进IEEE 33节点系统；长期规划成本独立报告，不能与储能年净成本直接计算节省比例
① 评估：区分典型日风险
② 短时：荷储协同与储能经济性
③ 长期：汇集–扩容联合规划
第二章：历史源荷与环境典型日
Chart: 季节
| 春 | 夏 | 秋 | 冬
综合得分 | 1.5978 | 1.674 | 1.5569 | 1.5828
最高：夏季 1.6740
设备电流与环境温度
热老化与日寿命损失
六项指标与AHP加权
同时刻画重载损伤与轻载利用不足
有序充电：储能容量减少27.96%
Chart: EV充电方式
| 无序充电 | 80%有序
储能容量 | 27.4 | 19.74
退役电池：年净成本降低46.90%
Chart: 电池类型（εev = 0.8）
| 新电池 | 退役电池
年净成本 | 298.65 | 158.57
短时治理综合得分：1.7258 → 0.2479
决策 | 方案
汇集变 | 节点14 / 3150 kVA
台区配变 | 2500 → 3150 kVA
汇集线路 | LGJ-120 / 18.988 km
Chart: 载流设备
| 台区配变 | 线路20-21 | 线路31-32
治理前 | 125.25 | 115.57 | 113.12
治理后 | 23.11 | 25.12 | 25.95
年规划成本：142.63万元
综合得分：43.1630 → 0.3638
部分设备仍略高于24 h参考值
Notes: Source: E:\application\xwechat_files\wxid_xyihcy7u0jkj21_d246\msg\file\2026-10\20261010170602.pdf
Assessment: PDF p.35 Table2-1 scores spring1.5978/summer1.6740/autumn1.5569/winter1.5828. Short-term: Tables3-5/3-6 PDF pp.53/55 capacities19.74/27.40 MWh; reduction=(27.40-19.74)/27.40=27.96%. PDF pp.51/53 EV simulation differs from Chapter2, baseline1.7258; PDF p.56 post-treatment0.2479. Net cost: Table3-7 p.58 new298.65 and retired158.57 wan CNY/year, same εev=.8; reduction46.90%. Long-term: p.71 constructed growth, not a forecasting validation; p.73 station14 3150kVA, transformer2500 to3150kVA, LGJ-120 18.988km, annual planning142.63. PDF p.74 Feq before125.25/115.57/113.12 h and after23.11/25.12/25.95 h, score43.1630 to.3638. Values above24h prevent a claim of full elimination. Annual storage net cost651.76 is not plotted or used for savings because its accounting differs. All numbers are reported or arithmetically derived from the thesis; not independently reproduced.